ISO 9001   IQNet CERTIFIED

Powerstar Rendszerfejlesztési és Fõvállalkozási Kft.

H-1039 Budapest, Nagyvárad u. 11-17.

Tel: (36-1)-2400-350, (36-1)-2400-352    Fax:  (36-1) 2400-349

Home-page: www.powerstar.hu  E-mail: office@powerstar.hu

Powerstar systems: built-in  „SETEEC TELECOM mini” with max 15A rectifier modules

System types:

TS19-48D105-4L/4U (NET), TS19-48D105-5L/4U (NET),, TS19-48D105-6L/4U (NET),  TS19-48D105-7L/4U (NET)

Remote monitoring: potential free contacts and serial RS232 communications or  SNMP  communications in case of  (NET) sign.

| DC standby systems for 19”racks. TS19-48D105-4L/4U (NET) 48V, 50A TS19-48D105-5L/4U (NET) 48V, 75A TS19-48D105-6L/4U (NET) 48V, 90A TS19-48D105-7L/4U (NET) 48V, 105A Egyenirányító 1 Egyenirányító 2 Egyenirányító 3 Vezérlés Standby systems with built-in batteries TSR-48D140-4L/9g (NET) 48V, 60A TSR-48D140-5L/9g (NET) 48V,75A TSR-48D140-6L/9g(NET) 48V,90A TSR-48D140-7L/9g(NET) 48V,105A | Technical details: 48V DC 60A, 75A, 90A, 105A, Input voltage: 230V,50Hz –15% +10% Input fuse: 32A ( C) circuit breaker D class peak voltage protection Power factor (Pf): 0.99 Output voltage 54V + 0.2% (float V 20°C) Ripple @ BW=30MHz 200mVp-p 20mVrms Sophomoric noise -52 db m over 600m (<2mV) Efficiency (nom. load) 90% @ 230 VAC Over voltage protection. 60 VDC Monitor signals Input and output voltage and current parameters Failure messages Remote signals by RS232 or SNMP for the working parameters and failure messages Failure signals with 3 pcs. of potential free contact - general failure - mains failure - Output voltage failure - Remote software with battery test function 3 pcs. of circuit breakers for DC distributor Deep charge level 42V (programmable) Module current sharing ±10% at nominal power DC distributors 3 pcs of circuit breakers Battery fuse 1 pc of 50A circuit breaker Dissipation max. 150W 19” rack W x H x D. 482 x 88 x 180mm (4U H. rack) Cabinet W x H x D . 530 x 1000 x 600mm (9g type) Mass: 2U high system 6 kg (built pass-in standard rack) Mass: battery system 48 kg (without batteries) Built-in possibility for the next type batteries: 4 peaces of 12V, 50Ah block batteries 4 peaces of 12V, 75Ah block batteries 4 peaces of 12V, 100Ah block batteries |
| --- | --- |

Expected life time of the built-in batteries is 10 years at 20 C° ambient temperature

AGM battery parameters:

Low internal resistor,, flammable cases,, high cycle number, low self discharge .VLRA

technology